## Theoretical Calcs
Phosphorus Precipitation Spreadsheet
User entered values = Yellow cells with blue font.
Green font indicates a variable name used within an equation. This spreadsheet uses named cells to simplify calculation tracking.
Chemical | Formula | Formula Weight, g/mole | Variable Name | Description | Typical Weight Percent in Commercial Solutions | Variable Name | Density, lb/gallon | Density, kg/L | Variable Name | Link to MSDS
Aluminum sulfate (Alum) - Liquid | Al2(SO4)3*14(H2O) | 594.3487 | MWAlum | Crystallized, dry form or liquid | 64.4 | PercentAlum | 11.1339 | 1.335 | DenseAlum | http://www.deltachemical.com/PDFS/DeltaAlumLiquid.pdf
Sodium Aluminate | Na2Al2O4 | 163.9402 | MWSodiumAluminate | Powder or liquid form | 31 | PercentNaAluminate | 12.0096 | 1.44 | DenseNaAluminate | http://www.deltachemical.com/PDFS/DeltaSodiumAluminate.pdf
Polyaluminum chloride (PAC) | [Al2(OH)nCl6－n·xH2O]m | 174.45 | MWPAC | Range in the degree of basicity and aluminum concentration | 51 | PercentPAC | 10.008 | 1.2 | DensePAC | http://msds.orica.com/pdf/shess-en-cds-020-000000015710.pdf
Ferric chloride | FeCl3 | 162.206 | MWFerricCl | Orange-brown aqueous solution | 40 | PercentFeCl2 | 11.8243 | 1.42 | DenseFeCl2 | http://www.sciencelab.com/msds.php?msdsId=9924035
Ferric sulfate | Fe2SO4 | 207.7516 | MWFerricSO4 | Green Aqueous Solution | 50 | PercentFeSO4 | 11.9262 | 1.43 | DenseFeSO4 | http://www.generalchemical.com/assets/msds/GC-7002.pdf
Lime | CaO | 56.0794 | MWLime | Dry white powder, CaO | NA
Slaked or Hydrated Lime | Ca(OH)3 | 91.1019 | MWSlaked | White slurry | NA
Note: P precipitation with lime or slaked lime is a function of pH, not Me.
Assume:
Medose/Pini | 2 | For Effluent P less than 1 mg/L. Value of 1.5 - 2 is typical to remove up to 98% of P.
Medose/Pini | 7 | For Effluent P lower than 0.5 mg/L. Value of 6 - 7 is typical.
Influent Flow | 1 | MGD | Qinf
Wastewater Alkalinity | 240 | mg/L as CaCO3 | Alkalinity
P at Secondary Effluent | 5 | mg/L as P | Pini
Desired effluent P | 0.75 | mg/L as P | Peff
Molecular Weight of Al | 26.9815 | g/mole | MWAl
Molecular Weight of Ca | 40.08 | g/mole | MWCa
Molecular Weight of Cl | 35.453 | g/mole | MWCl
Molecular Weight of Fe | 55.847 | g/mole | MWFe
Molecular Weight of H | 1.0079 | g/mole | MWH
Molecular Weight of Na | 22.9898 | g/mole | MWNa
Molecular Weight of O | 15.9994 | g/mole | MWO
Molecular Weight of P | 30.9738 | g/mole | MWP
Molecular Weight of S | 32.06 | g/mole | MWS
Step 1. Determine weight of Me available per liter of liquid chemical.
a. Find weight of chemical per liter of solution.
Chemical | Weight of Chemical in Kilograms per Liter | Units | Variable Name
Liquid Alum | 0.85974 | kg/L | WeightAlum |  | Conversion Factors
Sodium Aluminate | 0.4464 | kg/L | WeightNaAluminate |  | 10000 | mg/L in 1% solution
Polyaluminum chloride (PAC) | 0.612 | kg/L | WeightPAC |  | 1000 | mg/g
Ferric chloride | 0.568 | kg/L | WeightFeCl2 |  | 1000 | g/kg
Ferric sulfate | 0.715 | kg/L | WeightFeSO4 |  | mg/L = (10,000)(% w/w)(specific gravity)
b. Find weight of Me per liter of solution.
Chemical | Molecular Weight of Metal | Molecular Weight of Chemical | Ratio of Me/Chemical | Variable Name | Weight of Me in Grams per Liter | Variable Name
Liquid Alum | 26.9815 | 594.3487 | 0.090794 | AtoPAlum | 0.078059 | MeLAlum
Sodium Aluminate | 26.9815 | 163.9402 | 0.32916 | AtoPNaAluminate | 0.14694 | MeLNaAluminate
Polyaluminum chloride (PAC) | 26.9815 | 174.45 | 0.30933 | AtoPPAC | 0.18931 | MeLPAC
Ferric chloride | 55.847 | 162.206 | 0.3443 | FetoFeCl2 | 0.19556 | MeLFeCl2
Ferric sulfate | 55.847 | 207.7516 | 0.53763 | FetoFeSO4 | 0.38441 | MeLFeSO4
Step 2. Determine the weight of Fe or Aluminum required per unit weight of P.
a. Target dosage = | 1 | moles of Fedose per 1.0 mole P (Pini).
Note: Use a target dosage of 2 to remove P down to 1 mg/L.
Note: Use a target dosage of 7 mg/L to remove P down to 0.1 mg/L
Note: P must be in the ortho form for chemical precipitation to work. Organically bound P and poly-P will not be precipitated.
Parameter | Value | Units | Variable Name
b. Iron required = | 1.8 | kg Fe / kg P | FeRatio
c. Aluminum required = | 0.87 | kg Al / kg P | AlRatio
Step 3. Determine the amount of chemical solution required per kg P.
Chemical | liters solution / kg P | Variable Name
Liquid Alum | 11.1454 | LpKgAlum
Sodium Aluminate | 5.9208 | LpKgNaAluminate
Polyaluminum chloride (PAC) | 4.5956 | LpKgPAC
Ferric chloride | 9.2043 | LpKgFeCl2
Ferric sulfate | 4.6825 | LpKgFeSO4
Step 4. Determine the amount of chemical solution required per day.
a. Convert influent flow rate to Liters per day |  | 3785000 | QinfMetric
b. Calculate amount of chemical solution required per day.
Enter minimum days storage: | 30 | days
Chemical | Liters/day | Gallons/day | Feed Rate, gpm | Gallons per 30 days
Liquid Alum | 210.9 | 55.7 | 0.04 | 1671
Sodium Aluminate | 112.1 | 29.6 | 0.02 | 888
Polyaluminum chloride (PAC) | 87 | 23 | 0.02 | 690
Ferric chloride | 174.2 | 46 | 0.03 | 1380
Ferric sulfate | 88.6 | 23.4 | 0.02 | 702
Step 5. Estimate Storage Tank Footprint.
Assume: Cylindrical tank
Assume: Depth is equal to | 15 | feet
Chemical | Cubic Feet | Diameter, ft
Liquid Alum | 223.3957 | 4.3557
Sodium Aluminate | 118.7166 | 3.1752
Polyaluminum chloride (PAC) | 92.246 | 2.7989
Ferric chloride | 184.492 | 3.9583
Ferric sulfate | 93.8503 | 2.8232
Password: Indigo
Reference: EPA/600/R-10/100 (August 2010) Nutrient Control Design Manual
Reference: Metcalf and Eddy (2014) Wastewater Engineering, Treatment and Resource Recovery
Note on I6: Sidney: Same as specific gravity.
Note on B9: Sidney: Molecular formula may vary depending on manufacturer. m≤10, n=3~5
Note on C9: Sidney: Molecular weight taken from http://www.surechemical.com/watertreatment/polyaluchloride.html
Note on I11: Sidney: MSDS says 1.43 - 1.48